## Test Report
Inputs:
| Units | Imperial
| Target test pressure | 25 Pa
| Test Date | 2014-07-06
Client
| Building Description | John Smith's House
| Building Address (Street) | 12345 Broadway Street
| Building Address (City, State, ZIP code) | Everson, WA 98427
| Contact | Deborah Smith
| Phone | (360) 123-4567
[6 empty] | 1 | Total Duct Leakage
[7 empty] | Flow | Fan Pressure + Range Config
[6 empty] | 2 | Pressurization
25
Tester
| Company | Duct Testing Company
| Address (Street) | 12345 Main Street
| Address (City, State, ZIP code) | Everson, WA 98427
| Technician | Colin Genge
| Phone | (360) 738-9835
Equipment
| Retrotec fan series | 300
| Gauge Serial Number | 203460
| Fan Serial Number | FN1002509
Test data
| Conditioned Floor Area | 513
| Air Handler Flow | 600
| Leakage Exponent, n | 0.6
Baseline Pressure
Pressurization
| Duct Pressure | 25
| Range Configuration, or Enter "Flow" directly | (Enter Flow directly)
Fan Pressure
| Flow (from gauge) | 175.6
| Flow (calculated) | 175.6
Cost of Duct Leakage
| % of Duct Leakage to Outdoors | 60%
| Annual Cooling Cost | 1100
| Annual Heating Cost | 1500
| SEER rating | 10
|  | Supply | Return
| Average Duct Operating Pressure | 25 | 25
| Pressure Multiplier | 1 | 1
| Leakage Split | 0.5 | 0.5
| Leakage Penalty | 1 | 0.5
| Loss Factor | 0.5 | 0.25
Print/PDF preview:
Test Date: 2014-07-06
Duct Leakage
Test Report
|  |  |  | Client |  |  | Tester
|  |  | Building Description | John Smith's House |  | Company | Duct Testing Company
|  |  | Building Address | 12345 Broadway Street |  | Address | 12345 Main Street
|  |  |  | Everson, WA 98427 |  |  | Everson, WA 98427
|  |  | Contact | Deborah Smith |  | Technician | Colin Genge
|  |  | Phone | (360) 123-4567 |  | Phone | (360) 738-9835
|  |  | Test Type | Total Duct Leakage |  | Gauge S/N | 203460
|  |  | Fan series | 300 |  | Fan S/N | FN1002509
Building and Duct Details
[5 empty] | Conditioned Floor Area | 513
[5 empty] | Air Handler Flow | 600
[5 empty] | Percentage of Duct Leakage to Outdoors | 60%
[5 empty] | Supply | Return
|  |  |  | Average Duct Operating Pressure | 25 | 25
|  |  |  | Leakage Split | 50% | 50%
|  |  |  | Leakage Penalty | 100% | 50%
Leakage Data
Baseline Pressure
Pressurization
|  |  |  | Duct Pressure | 25
Fan Pressure
|  |  |  | Range Configuration | (Enter Flow directly)
|  |  |  | Duct Leakage | 175.6
|  |  |  | Leakage Area | 32.6546
|  |  |  | Leakage constant, C | 25.4543
|  |  |  | Leakage Exponent | 0.6
Leakage Results
|  |  |  | Total Duct Leakage | 175.6
|  |  |  | Duct Leakage as % of Air Handler Flow | 29.27%
|  |  |  | Duct Leakage to Outdoors (estimated) | 105.36
|  |  |  | Leakage Area | 32.6546
|  |  |  | Leakage/Conditioned Floor Area | 0.3423
34.23
342.3002
Cost of Duct Leakage
|  |  |  | HVAC System Efficiency Loss | 13.17%
|  |  |  | Annual Cooling Loss | 144.87
|  |  |  | Annual Heating Loss | 197.55
|  |  |  | Annual Operating SEER | 8.683
DucTester flow equation
Flow (cfm)= (PrB - PrA*K1)N * (K + PrB*K3)
|  | where: | PrA = Induced pressure
PrB = Fan pressure (difference between pressure sensor inside the fan, and pressure sensor
outside the fan on the suction side of the Fan Shell)
|  | Range | DucTester flow equation constants |  |  |  |  | Min PrB
|  | Ring | N | K | K1 | K2 | K3 | (Pa)
| Model 200. | Open- | 0.5115 | 30.7774 | 0 | 0.2 | 0 | 10
|  | Mid | 0.5415 | 5.9146 | 0 | 0.5 | 0 | 25
|  | Low | 0.6125 | 1.0056 | -0.024 | 0.5 | -0.0002 | 25
(Enter Flow directly)
| Model 300- | Open. | 0.515 | 27.9 | 0 | 0.04 | 0 | 10
|  | 102 | 0.51 | 17 | 0.001 | 0.072 | -0.0002 | 18
|  | 74 | 0.5 | 7.05 | 0 | 0.16 | 0.0001 | 40
|  | 47 | 0.5 | 2.94 | -0.01 | 0.1 | 0.0001 | 25
|  | 29 | 0.5 | 1.192 | 0 | 0.036 | 0 | 9
|  | 18 | 0.5 | 0.442 | -0.01 | 0.14 | 0 | 35
|  | 11 | 0.53 | 0.1464 | -0.07 | 0.18 | 0 | 45
|  | 7 | 0.445 | 0.081 | 0 | 0.1 | 2e-05 | 25
|  | 3 | 0.445 | 0.018118 | 0 | 0.1 | 7e-06 | 25
(Enter Flow directly)
negative Channel A coeffcients not added for Model 300 yet
* DucTester Fan pressure "PrB" must be greater than "Min Fan Pressure" and greater than (PrA*K2)
Note on C32: Enter the "n" value, as read from the top bar of the DM-2 gauge. If you are unsure of which value to use, enter 0.60
Note on C46: When performing a Total Duct Leakage test, you must enter a value here if you want to estimate a result for Duct Leakage to Outdoors
Note on C38: This number is the "PrA" reading on the DM-2, or the top row measurement on the DM32 gauge. If the Baseline function on the gauge is used, the Baseline must be cleared. If you are using Retrotec's "Method 2" or "Method 3" (setting the pressure between the duct system and the house to 0 Pa), enter 25 or -25 Pa (Duct Pressure relative to outdoors), NOT 0 Pa. Method 2 and Method 3 are described in section 4.2.2 and section 4.2.3, respectively, in Manual-DucTester Operation & Testing.
Note on C31: This is the total air flow through the duct system. (This field is optional: Input this only if you want the report to display the Duct Leakage as a percentage of the Air Handler Flow) If you do not know the Air Handler Flow, there is a method to calculate it, which is described in Appendix F of Manual-DucTester Operation & Testing
Note on C30: The area that is normally air-conditioned or heated (i.e. inside the enclosure envelope). Even though supply ducts may not discharge directly into these spaces, they are considered “conditioned” if their temperature follows indoor temperature closer than outdoor temperature.
Note on C2: Imperial: CFM, ft2, in2 Metric: m3/h, m2, cm2
Note on C6: Date format: YYYY-MM-DD YYYY=Year MM=Month DD=Day
Duct Leakage Test Reporting software rev-2014-08-18 Instructions: 1. Macros must be enabled: i. Click the "Options…" button (by the Security Warning, on the tool bar above) ii. Select "Enable this content" iii. Click "OK" 2. Fill out the green cells only. The "Cost of Duct Leakage" section is optional. 3. To save the Duct Leakage Test Report as a PDF file, click  mouseover "Save As"  "PDF or XPS"  "Publish" For detailed instruction on using this software, refer to section 8 of Retrotec's Manual-DucTester Operation & Testing, which can be downloaded at the following link: http://retrotec.com/Downloads/WebsitePDFs/Manual-DucTester Operation & Testing.pdf
% of Duct Leakage to Outdoors: Enter the estimated percentage of the Total Duct leakage that leads to outdoors in order to estimate Cost of Duct Leakage. (Input is only required when performing a Total Duct Leakage test) Annual Cooling Cost: Enter the cooling cost per year from the utility bill. This entry is used to estimate the cost of Duct Leakage to Outdoors included in the cooling bill. Annual Heating Cost: Enter heating cost per year from the utility bill. This entry is used to estimate the cost of Duct Leakage to Outdoors included in the heating bill. Average Duct Operating Pressure: Measure the pressure in the supply duct closest to the plenum and enter that pressure to get an accurate calculation of duct losses. Do the same for the return. Using the test pressure (default value) here will not be as accurate. Leakage Split: Enter the estimated fraction of the Total Duct Leakage that is on the supply side and the return side. Their default values are 0.5, meaning the leakage of the HVAC system is split evenly between the supply and return. The Leakage Split for the supply side and the return side always add up to 1.0. Supply Leakage Penalty: This is the estimated fraction of energy loss of the supply side. The default value is 1.0. This means that of the supply air leakage, all of its energy is lost to the outdoors (i.e. none of its energy is returned back into the house). This number can be lowered if some of the energy from duct leakage leads back into the house. For example, if supply leaks are going into a wall cavity, some of the energy loss will be regained back into the house, so a lower leakage penalty would provide a better estimate of annual HVAC losses. Return Leakage Penalty: This is the estimated fraction of energy loss of the return side. The default value is 0.5, which assumes that of the return air leakage, about half of its energy is lost to outdoors (i.e. the other half of its energy is regained back into the house). This number can be raised if you suspect that there is actually more energy loss to the outdoors from the return side. For example, if the return goes through a very cold crawl space, the return leakage would pull in cold air and have a greater effect on the annual HVAC losses. *The "Annual Cooling Loss" and "Annual Heating Loss" in the report are for estimation purposes only

## Requirements (hidden)
Duct leakage program requirements
Abu Dhabi Building Code | Total Duct Leakage: 12 CFM25/100 ft2 of conditioned floor area Duct Leakage to Outdoors: 8 CFM25/100 ft2 of conditioned floor area
Energy Star | Total Duct Leakage: 6.0 CFM25/100 ft2 of conditioned floor area Duct Leakage to Outdoors: 4.0 CFM25/100 ft2 of conditioned floor area.
International Energy Conservation Code | Total Duct Leakage: 12 CFM25/100 ft2 conditioned floor area Duct Leakage to Outdoors: 8 CFM25/100 ft2 conditioned floor area 6 CFM25/100 ft2 after rough in (after ducts are installed but no sheet rock and with air handler) Required: • Where ducts are located outside the conditioned space • In existing houses where more than 50% of the ducts are replaced Not required if all connections meet Code requirements and visually inspected by licensed contractor or DET verifier.
New York Energy Code | Total Duct Leakage: 6.0 CFM25/100 ft2 of conditioned floor area or 6% of airhandler flow. Measured at supply closest to air handler. Test equipment must be certified by manufacturer (complies with ASTM E1554-07 and ASHRAE Standard 152). Duct leakage to outdoors acceptable under Method A of ASMT E1554-07.
North Carolina Energy Code | Total Duct Leakage: 6.0 CFM25/100 ft2 of conditioned floor area. Depressurize to -25 Pa measured at supply closest to air handler. Test equipment must be certified by manufacturer that it complies with ASTM E1554-07. No mention of duct leakage to outdoors testing being acceptable.
North West Energy Star (ID, MO, OR, WA states) | Total Duct Leakage: 0.06 CFM50/ft2 of conditioned floor area or 75CFM, whichever is greater. House leakage must be less than or equal to 4 ACH50.
Title 24 | Maximum duct leakage is 15% of airhandler flow calculated by using 400 CFM25 per Ton or 21.7 CFM per 1000 BTU. Test pressure +25Pa. Maximum duct leakage is 60CFM/Ton or 3.255 CFM/1000 BTU 105 CFM25/1000 ft2 of floor area for climate zones 8 through 15. 75 CFM25/1000 ft2 of floor area for climate zones 7 and 16.
Washington Energy Code | Total Duct Leakage: with air handler NOT installed= floor area (ft2) X 0.04 CFM25 with air handler installed= floor area (ft2) X 0.06 CFM25 Duct Leakage to Outdoors: = floor area (ft2) X 0.08 CFM25 is recommended where possible.