## Simulation
If Stack Pressure is estimated/measured, this simulation can be used to estimate: 1. How large of an opening (leakage area) from the first floor will ensure interior pressure difference is less than 10% (required by the USACE standard) 2. The fan flow required 3. The error of this flow estimation if there is no stack pressure and no interior constriction
Enter values into Green boxes only
[7 empty] | Leakage of building | 0.25
[7 empty] | Stack Pressure at 1st floor | -10
[7 empty] | Area of pinch point from 1st floor to upper floors | 28
|  |  | Pressurization Target | 75 | [6 empty] | Depressurization Target | -75
[19 empty] | walls |  | top + bottom | bottom | Total area | CFM/ | CFM at
[16 empty] | width | depth | ht | sq. ft. | # doors | sq. ft. | sq. ft. | sq. ft. | sq. ft. | 75 | C
[15 empty] | whole building | 300 | 120 | 100 | 84000 |  | 72000 |  | 156000 | 0.25 | 39000 | 2924.3399
[15 empty] | top above fan floor | [10 empty] | 2013.2955
[15 empty] | bottom floor with fans |  |  | 15 | 12600 |  |  | 36000 | 48600 | 0.25 | 12150 | 911.0444 | Assumed that all stack is dropped across this hole which is not true but simple enough to allow a calculation.
[15 empty] | Bottom to Top doorways | 2 |  | 7 |  | 2 |  |  | 28
[15 empty] | + other pathways, chases, shafts, leaks | [7 empty] | 0
[15 empty] | Total | [7 empty] | 28 |  |  | 4334.4
[17 empty] | Pre test with Fans covered |  |  |  |  | Blower Door results with Stack and interior Pressure Differences
[16 empty] | Pressure | Bldg leakage |  | Stack |  | + Pressurize | Flow | % P difference |  | - Depressurize | Flow | % P difference
[16 empty] | on gauge | n | C | Flow |  |  | CFM | from avg |  |  | CFM | from avg
| 100 | [7 empty] | 100
[16 empty] | Stack | [7 empty] | with Stack
[20 empty] | Test pressure Target | 75 | 0 |  |  | -75
[15 empty] | Stack at top | 2.6672 | 0.6 | 2013.2955 | 3626.9329 | Gauge,Top to outdoors | 52.9233 | 21781.9014 |  |  | -64.3935 | 24502.6295
[20 empty] | Gauge, Top ref'd to bottom | 50.2561 |  |  |  | -67.0607
[20 empty] | Top less Bias | 60.2561 |  | -10.9% |  | -57.0607 |  | -13.58%
[17 empty] | 0.6 | 4334.4 |  | Gauge across doorways | 14.7439 | 21781.9014 |  |  | 17.9393 | 24502.6295
[15 empty] | Stack at bottom | -10 | 0.6 | 911.0444 | 3626.9329 | Gauge, Bottom to outdoors | 65 | 11150.3252 |  |  | -85 | 13097.5744
[20 empty] | Test Point at Avg Pressure | 67.6281 | 32932.2266 |  |  | -66.0303 | 37600.2039 |  | Maximum | 40586.4302 | CFM Test fan flow to achieve | 75 | Pa
[6 empty] | 15 | [7 empty] | 15 | [5 empty] | Bottom less Bias | 75 | 35041.4175 | 10.9% |  | -75 | 40586.4302 | 13.58% | Average | 37813.9238 | CFM
[20 empty] | Error from True |  | -10.15% |  |  |  | 4.068% |  |  | -3.041% | error when test both directions
[16 empty] | Stack is ZERO | [7 empty] | 0 Stack
[20 empty] | Test pressure Target | 75 |  |  |  | -75
[16 empty] | 0 | 0.6 | 2013.2955 | 0 | Gauge,Top to outdoors | 58.6584 | 23168.9139 |  |  | -58.6584 | 23168.9139
[16 empty] | 0 |  |  |  | Gauge, Top ref'd to bottom | 58.6584 |  |  |  | -58.6584 |  | -12.23%
[20 empty] | Top less Bias | 58.6584 |  | -12.23%
[17 empty] | 0.6 | 4334.4 |  | Gauge across doorways | 16.3416 | 23168.9139 |  |  | 16.3416 | 23168.9139
[20 empty] | Gauge, Bottom to outdoors | 75 | 12150
[16 empty] | 0 | 0.6 | 911.0444 | 0 | [5 empty] | -75 | 12150 | 12.23%
[20 empty] | Test Point at Avg Pressure | 66.8292 | 35318.9139 |  |  | -66.8292 | 35318.9139 |  | Maximum | 37849.8649 | CFM Test fan flow to achieve | 75 | Pa
[20 empty] | Bottom less Bias | 75 | 37849.8649 | 12.23% |  | 75 | 37849.8649 |  | Average | 37849.8649 | CFM
[20 empty] | Error from True |  | -2.949% |  |  |  | -2.949% |  |  | -2.949% | error when test both directions
[28 empty] | TRUE | 39000 | CFM
|  | 120 | [7 empty] | 120
|  |  | Interior pressure difference: | 10.9% | [6 empty] | Interior pressure difference: | 13.58%
[5 empty] | 300 | [7 empty] | 300
*Dimensions are not shown to scale
53 Pa
35,041 CFM
-10.2%
50 Pa
65 Pa
15 Pa
40,586 CFM
4.1%
-85 Pa
28 sq ft
28 sq ft
-64 Pa
-67 Pa
18 Pa
Note on AD15: Colin Genge: How many doorways lead from bottom floor with Test Fans to upper portion of building
Note on AG15: Stephen Wong: Sum of w + h + # of doors But for simulation, this will be an input
Note on AD31: Colin Genge: Average pressure, total Test Fan flow to outdoors
Note on AG32: Stephen Wong: USACE: Pressures in the extremeties cannot be greater than 10% from average induced envelope pressure
Note on AF33: Stephen Wong: Error as a result of stack and constriction (when compared to no stack and no constriction)
Note on AD42: Colin Genge: Average pressure, total Test Fan flow to outdoors

## Use this (2) (hidden)
Enter values into Green boxes only: |  |  | Press | Depress
|  |  |  | walls |  | top + bottom | bottom | Total area | CFM/ | CFM at
| width | depth | ht | sq. ft. | # doors | sq. ft. | sq. ft. | sq. ft. | sq. ft. | 75 | C
whole building | 300 | 120 | 100 | 84000 |  | 72000 |  | 156000 | 0.25 | 39000 | 2924.3399
top above fan floor | [10 empty] | 2013.2955
bottom floor with fans |  |  | 15 | 12600 |  |  | 36000 | 48600 | 0.25 | 12150 | 911.0444 | Assumed that all stack is dropped across this hole which is not true but simple enough to allow a calculation.
Bottom to Top doorways | 2 |  | 7 |  | 2 |  |  | 28
+ other pathways, chases, shafts, leaks | [7 empty] | 0
Total | [7 empty] | 28 |  |  | 4334.4
|  | Pre test with Fans covered |  |  |  |  | Blower Door results with Stack and interior Pressure Differences
| Pressure | Bldg leakage |  | Stack |  | + Pressurize | Flow | % P difference |  | - Depressurize | Flow | % P difference
| on gauge | n | C | Flow |  |  | CFM | from avg |  |  | CFM | from avg
| Stack | [7 empty] | with Stack
[5 empty] | Test pressure Target | 75 | 0 |  |  | -75
Stack at top | -6.668 | 0.6 | 2013.2955 | 6284.9746 | Gauge,Top to outdoors | 72.9961 | 26417.2349 |  |  | -44.3207 | 19582.6512
[5 empty] | Gauge, Top ref'd to bottom | 79.6641 |  |  |  | -37.6527
[5 empty] | Top less Bias | 54.6641 |  | -15.68% |  | -62.6527 |  | -8.97%
|  | 0.6 | 4334.4 |  | Gauge across doorways | 20.3359 | 26417.2349 |  |  | 12.3473 | 19582.6512
Stack at bottom | 25 | 0.6 | 911.0444 | 6284.9746 | Gauge, Bottom to outdoors | 100 | 14439.0799 |  |  | -50 | 9526.2401
[5 empty] | Test Point at Avg Pressure | 64.832 | 40856.3148 |  |  | -68.8264 | 29108.8913 |  | Maximum | 44588.4267 | CFM Test fan flow to achieve | 75 | Pa
[5 empty] | Bottom less Bias | 75 | 44588.4267 | 15.68% |  | -75 | 30648.5206 | 8.97% | Average | 37618.4737 | CFM
[5 empty] | Error from True |  | 14.33% |  |  |  | -21.41% |  |  | -3.542% | error when test both directions
| Stack is ZERO | [7 empty] | 0 Stack
[5 empty] | Test pressure Target | 75 |  |  |  | -75
| 0 | 0.6 | 2013.2955 | 0 | Gauge,Top to outdoors | 58.6584 | 23168.9139 |  |  | -58.6584 | 23168.9139
| 0 |  |  |  | Gauge, Top ref'd to bottom | 58.6584 |  |  |  | -58.6584 |  | -12.23%
[5 empty] | Top less Bias | 58.6584 |  | -12.23%
|  | 0.6 | 4334.4 |  | Gauge across doorways | 16.3416 | 23168.9139 |  |  | 16.3416 | 23168.9139
[5 empty] | Gauge, Bottom to outdoors | 75 | 12150
| 0 | 0.6 | 911.0444 | 0 | [5 empty] | -75 | 12150 | 12.23%
[5 empty] | Test Point at Avg Pressure | 66.8292 | 35318.9139 |  |  | -66.8292 | 35318.9139 |  | Maximum | 37849.8649 | CFM Test fan flow to achieve | 75 | Pa
[5 empty] | Bottom less Bias | 75 | 37849.8649 | 12.23% |  | 75 | 37849.8649 |  | Average | 37849.8649 | CFM
[5 empty] | Error from True |  | -2.949% |  |  |  | -2.949% |  |  | -2.949% | error when test both directions
[13 empty] | TRUE | 39000 | CFM
Note on F7: Colin Genge: How many doorways lead from bottom floor with Test Fans to upper portion of building
Note on I9: Stephen Wong: Area of pinch point from 1st floor to Upper Floors
Note on F23: Colin Genge: Average pressure, total Test Fan flow to outdoors
Note on F34: Colin Genge: Average pressure, total Test Fan flow to outdoors

## Use this (hidden)
Enter values into dark colors only: |  |  | Press | Depress
|  |  |  | walls |  | top + bottom | bottom | Total area | CFM/ | CFM at
| width | depth | ht | sq. ft. | # | sq. ft. | sq. ft. | sq. ft. | sq. ft. | 75 | C
whole building | 300 | 120 | 100 | 84000 |  | 72000 |  | 156000 | 0.25 | 39000 | 2924.3399
top above fan floor | [10 empty] | 2013.2955
bottom floor with fans |  |  | 15 | 12600 |  |  | 36000 | 48600 | 0.25 | 12150 | 911.0444
Bottom to Top doorways | 3 |  | 7 |  | 2 |  |  | 42
+ other pathways, chases, shafts, leaks | [7 empty] | 0
Total | [7 empty] | 42 |  |  | 6501.6
|  | Before Blower Door |  |  |  |  | Blower Door results with Stack and interior Pressure Differences
| Pressure | Bldg leakage |  | Stack |  | + Pressurize | Flow | % P difference |  | - Depressurize | Flow | % P difference
| on gauge | n | C | Flow |  |  | CFM | from avg |  |  | CFM | from avg
| Stack | [7 empty] | with Stack
[5 empty] | Test pressure Target | 50 | 1.4552e-11 |  |  | -50
Stack at top | 6.668 | 0.6 | 2013.2955 | 6284.9746 | Gauge,Top to outdoors | 27.7367 | 14782.2421 |  |  | -59.8493 | 23449.999
[5 empty] | Gauge, Top ref'd to bottom | 21.0687 |  |  |  | -66.5172
[5 empty] | Top less Bias | 46.0687 |  | -4.092% |  | -41.5172 |  | -9.269%
|  | 0.6 | 6501.6 |  | Gauge across doorways | 3.9313 | 14782.2421 |  |  | 8.4828 | 23449.999
Stack at bottom | -25 | 0.6 | 911.0444 | 6284.9746 | Gauge, Bottom to outdoors | 25 | 6284.9746 |  |  | -75 | 12150
will be set as Bias (Baseline in the software)
[5 empty] | Test Point at Avg Pressure | 48.0344 | 21067.2167 |  |  | -45.7586 | 35599.999 |  | Maximum | 37544.6675 | CFM Test fan flow to achieve | 50 | Pa
[5 empty] | Bottom less Bias | 50 | 21580.3233 | 4.092% |  | -50 | 37544.6675 | 9.269% | Average | 29562.4954 | CFM
[5 empty] | Error from True |  | -29.43% |  |  |  | 22.78% |  |  | -3.321% | error when test both directions
| Stack is ZERO | [7 empty] | 0 Stack
[5 empty] | Test pressure Target | 50 |  |  |  | -50
| 0 | 0.6 | 2013.2955 | 0 | Gauge, Top to outdoors | 43.793 | 19442.4155 |  |  | -43.793 | 19442.4155
| 0 |  |  |  | Gauge, Top ref'd to bottom | 43.793 |  |  |  | -43.793
[5 empty] | Top less Bias | 43.793 |  | -6.618% |  | -43.793 |  | -6.618%
|  | 0.6 | 6501.6 |  | Gauge across doorways | 6.207 | 19442.4155 |  |  | 6.207 | 19442.4155
[5 empty] | Gauge, Bottom to outdoors | 50 | 9526.2401 |  |  | -50 | 9526.2401
| 0 | 0.6 | 911.0444 | 0 | [7 empty] | 6.618%
[5 empty] | Test Point at Avg Pressure | 46.8965 | 28968.6555 |  |  | -46.8965 | 28968.6555 |  | Maximum | 30104.1344 | CFM Test fan flow to achieve | 50 | Pa
[5 empty] | Bottom less Bias | 50 | 30104.1344 | 6.618% |  | 50 | 30104.1344 |  | Average | 30104.1344 | CFM
[5 empty] | Error from True |  | -1.55% |  |  |  | -1.55% |  |  | -1.55% | error when test both directions
[13 empty] | TRUE | 30578.0546 | CFM
Note on F7: Colin Genge: How many doorways lead from bottom floor with Test Fans to upper portion of building
Note on F23: Colin Genge: Average pressure, total Test Fan flow to outdoors
Note on F34: Colin Genge: Average pressure, total Test Fan flow to outdoors