## Error from @ Pressure
Error from @ Pressure
When the desired reference (or test pressure) cannot be achieved, the Retrotec Gauge or software will calculate what the result would be if that pressure could be achieved.
The calculation below shows what the maximum and minimum errors could be. This does not take into account error contributions from wind or Baseline that might increase the error slightly.
Instructions
Enter values only in the green boxes. Results in yellow box show the worst case errors but typically errors will be much less or could be zero.
type of test | Assumed n value | min. n | max. n | Gauge errors, % of reading | Actual test pressure | Flow measured at actual test pressure | Desired test pressure | Flow displayed @ desired test pressure | Lowest possible flow at desired test pressure |  | Highest possible flow at desired test pressure
[5 empty] | Pa or in WC |  | Pa or in WC
Residential Duct testing | 0.6 | 0.5 | 0.7 | 1% | 15 | 324 | 25 | 440.2043 | 414.1201 | -5.925% | 469.807 | 6.725%
Commercial Duct testing | 0.65 | 0.55 | 0.75 | 1% | 4.2 | 290 | 6 | 365.6657 | 348.993 | -4.56% | 384.6707 | 5.197%
Residential house testing | 0.65 | 0.55 | 0.75 | 1% | 25 | 800 | 50 | 1255.3346 | 1158.4548 | -7.717% | 1365.7686 | 8.797%
LargeBuilding testing | 0.6 | 0.5 | 0.7 | 1% | 25 | 7500 | 50 | 11367.8742 | 10501.0608 | -7.625% | 12355.5643 | 8.688%
Form of leakage equation | Flow = Constant X Test Pressure n where "n" is the exponent in a power equation.
Enter any desired value in the green boxes to get answers in the yellow boxes.
The “Error from @ Pressure” tab shows the range of errors that could occur when testing to a lower pressure when you desire a result at a higher pressure. An example would be if you wanted to test a building at 50 Pa but could achieve only 25 Pa; the spreadsheet on Row 10 shows that the error could be -7.7% to +8.8% due to having to assume the exponent, n in the equation. The Assumed Values for Residential Ducts and Large Buildings are both 0.6 but Commercial Ducts and Residential Houses use 0.65.
In addition, the effects of gauge error is also shown where if the test pressure gauge had the maximum error in one direction while the flow pressure gauge had the maximum error in the other direction, a resultant error could be combined to uncover the worst case for negative and postive error that can be added to the @ Pressure potential error.

## Commercial Ducts
Error from @ Pressure
When the desired reference (or test pressure) cannot be achieved, the Retrotec Gauge or software will calculate what the result would be if that pressure could be achieved.
The calculation below shows what the maximum and minimum errors could be. This does not take into account error contributions from wind or Baseline that might increase the error slightly.
Instructions
Enter values only in the green boxes. Results in yellow box show the worst case errors but typically errors will be much less or could be zero.
type of test | Assumed n value | min. n | max. n | Gauge errors, % of full scale | Full scale | Actual test pressure | Flow pressure measured on gauge | Flow measured at actual test pressure | Desired test pressure | Flow displayed @ desired test pressure | Lowest possible flow at desired test pressure |  | Highest possible flow at desired test pressure
|  |  |  | 1% | 10 | in WC |  |  | in WC
Commercial Duct testing | 0.65 | 0.55 | 0.75 |  | 0.1 | 4 | 4 | 290 | 6 | 377.4482 | 352.6165 | -6.579% | 408.0899 | 8.118%
Form of leakage equation | Flow = Constant X Test Pressure n where "n" is the exponent in a power equation.
Enter any desired value in the green boxes to get answers in the yellow boxes.
The “Error from @ Pressure” tab shows the range of errors that could occur when testing to a lower pressure when you desire a result at a higher pressure. An example would be if you wanted to test a building at 50 Pa but could achieve only 25 Pa; the spreadsheet on Row 10 shows that the error could be -7.7% to +8.8% due to having to assume the exponent, n in the equation. The Assumed Values for Residential Ducts and Large Buildings are both 0.6 but Commercial Ducts and Residential Houses use 0.65.
In addition, the effects of gauge error is also shown where if the test pressure gauge had the maximum error in one direction while the flow pressure gauge had the maximum error in the other direction, a resultant error could be combined to uncover the worst case for negative and postive error that can be added to the @ Pressure potential error.
This spreadsheets shows error as % of full scale

## EqLA
Canadian EqLA
Equivalent Leakage Area is normally measured at 10 Pa but EqLA values at higher pressures such as 50 Pa are much more stable.
This shows how to convert any flow rate at any pressure to EqLA10 and EqLA50. You'll notice that when n= 0.5, the EqLAs are all the same. Typically a default for n would be 0.65 for typical houses.
Actual Test Pressure = | 10 | Pa |  |  | Actual Test Pressure = | 10 | Pa
Flow at this Test Pressure = | 100 | CFM |  |  | Flow at this Test Pressure = | 100 | liter/s
n = | 0.5 |  |  |  | n = | 0.5
EqLA = | 29.4165 | sq. inches | 10 | Pa | EqLA = | 90.7901 | sq. cm. | 10 | Pa
EqLA = | 29.4165 | sq. inches | 50 | Pa | EqLA = | 90.7901 | sq. inches | 50 | Pa
Actual Test Pressure = | 10 | Pa |  |  | Actual Test Pressure = | 10 | Pa
Flow at this Test Pressure = | 100 | CFM |  |  | Flow at this Test Pressure = | 100 | liter/s
n = | 0.65 |  |  |  | n = | 0.65
EqLA = | 29.4165 | sq. inches | 10 | Pa | EqLA = | 90.7901 | sq. cm. | 10 | Pa
EqLA = | 37.4487 | sq. inches | 50 | Pa | EqLA = | 115.5803 | sq. inches | 50 | Pa
Actual Test Pressure = | 50 | Pa |  |  | Actual Test Pressure = | 50 | Pa
Flow at this Test Pressure = | 223.4 | CFM |  |  | Flow at this Test Pressure = | 223.4 | liter/s
n = | 0.5 |  |  |  | n = | 0.5
EqLA = | 29.3893 | sq. inches | 10 | Pa | EqLA = | 90.7061 | sq. cm. | 10 | Pa
EqLA = | 29.3893 | sq. inches | 50 | Pa | EqLA = | 90.7061 | sq. inches | 50 | Pa

## EfLA
US EfLA
Effective Leakage Area is normally measured at 10 Pa but EfLA values at higher pressures such as 50 Pa are much more stable.
This shows how to convert any flow rate at any pressure to EfLA10 and EfLA50. You'll notice that when n= 0.5, the EfLAs are all the same. Typically a default for n would be 0.65 for typical houses.
Actual Test Pressure = | 4 | Pa |  |  | Actual Test Pressure = | 4 | Pa
Flow at this Test Pressure = | 100 | CFM |  |  | Flow at this Test Pressure = | 100 | liter/s
n = | 0.5 |  |  |  | n = | 0.5
EfLA = | 28.4186 | sq. inches | 4 | Pa | EfLA = | 87.7101 | sq. cm. | 4 | Pa
EfLA = | 28.4186 | sq. inches | 50 | Pa | EfLA = | 87.7101 | sq. inches | 50 | Pa
Actual Test Pressure = | 4 | Pa |  |  | Actual Test Pressure = | 4 | Pa
Flow at this Test Pressure = | 100 | CFM |  |  | Flow at this Test Pressure = | 100 | liter/s
n = | 0.65 |  |  |  | n = | 0.65
EfLA = | 28.4186 | sq. inches | 4 | Pa | EfLA = | 87.7101 | sq. cm. | 4 | Pa
EfLA = | 41.5087 | sq. inches | 50 | Pa | EfLA = | 128.1109 | sq. inches | 50 | Pa
Actual Test Pressure = | 50 | Pa |  |  | Actual Test Pressure = | 50 | Pa
Flow at this Test Pressure = | 223.4 | CFM |  |  | Flow at this Test Pressure = | 223.4 | liter/s
n = | 0.5 |  |  |  | n = | 0.5
EfLA = | 17.9569 | sq. inches | 4 | Pa | EfLA = | 55.4214 | sq. cm. | 4 | Pa
EfLA = | 17.9569 | sq. inches | 50 | Pa | EfLA = | 55.4214 | sq. inches | 50 | Pa